FIRE/SMOKE DAMPER MAINTENANCE RECORD

Date: __________                                              Inspector: ______________________________

Location: ____________________________________________________________________

This is to certify that the following testing and maintenance was performed on the dampers listed. Any modifications or repairs made are described below.

Y = Satisfactory                 N = Unsatisfactory                 N/A = Not applicable

| Damper number or location | Damper Type | Tested | Fully Closed | Latch Checked | Fusible Link Removed | Moving Parts Lubricated |
| --- | --- | --- | --- | --- | --- | --- |

COMMENTS: _____________________________________________________________________

_________________________________________________________________________________

_________________________________________________________________________________

_________________________________________________________________________________

FIRE/SMOKE DAMPER MAINTENANCE RECORD

Date: December 24, 2008                                      Inspector: John J. Smith, Smith Heating & AC

Location: Any Town Nursing Home, Anyplace, MN____________________________________

This is to certify that the following testing and maintenance was performed on the dampers listed. Any modifications or repairs made are described below.

Y = Satisfactory                 N = Unsatisfactory                 N/A = Not applicable

| Damper number or location | Damper Type | Tested | Fully Closed | Latch Checked | Fusible Link Removed | Moving Parts Lubricated |
| --- | --- | --- | --- | --- | --- | --- |
| South Wing smoke barrier | Smoke | Y | N1 | N/A | N/A | Y |
| Fire barrier wall into apt. bldg. | Smoke/fire | Y | Y | Y | Y | Y |
| Air duct between 3rd & 4th flrs. | Fire | Y | Y | Y | Y | Y |

COMMENTS: 1Damper control arm found disconnected – damper wouldn’t close – repaired and retested OK

_________________________________________________________________________________

_________________________________________________________________________________

_________________________________________________________________________________